O & M Manual

and

Preventive Maintenance Logs

For Small Water & Wastewater Systems

Prepared by Wyoming Assn. of Rural Water Systems

This format / template is the property of WARWS, has been produced as a  membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

WARWS wishes to acknowledge and thank Florida Rural Water Association who graciously allowed WARWS the use of their template for modification and use in Wyoming. .

Water System:___________________________________________________

Street Address:______________________________________________________

City, State, Zip:______________________________________________________

Phone:___________________________ Fax:___________________________

Contact:________________________________________________________

E-mail:_________________________________________________________

Number Connections:_______________

PWS:_____________________________

County:____________________________

Classification: Community______ Non-Community______ NTNC______

Source: Ground ______Surface______ Purchased_______

Ownership:______________________________________________________

Date:____________________________

307-436-8636   warws.com

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

WARWS wishes to acknowledge and thank Florida Rural Water Association who graciously allowed WARWS the use of their template for modification and use in Wyoming.

Section ...................................................................Section Description   Page

Preface.......................................................................

Operation & Maintenance Manual	  					  4

Preventive Maintenance Log

Section 1 ...................................................... Maintenance Contacts List   5

Service / Repair Contacts

Section 2 ............ Bound & Indexed Equipment Manufacturer Manuals  6

System Description & Major Equipment

Source or Sources of Water (Wells)

Types of Treatment

Major Controls

Storage & Distribution Features

Section 3 ............................................ Preventive Maintenance Log   7 - 19

Recommended Daily Preventive Maintenance

Recommended Weekly Preventive Maintenance

Recommended Monthly Preventive Maintenance

Preventive Maintenance Recommendations

Suggested Preventive Maintenance Logs

Section 4 ................................................ Emergency Response Plan *    20

Emergency Response Plan Template…....pages  21-32

Section 5  .......................................... Permits & Specific Conditions *    33

Section 6  ......................................... System Description & Reports *     34

Section 7  ............................... General System Operation & Control *    35

Section 8  ............................................................. Laboratory Testing *    36

Section 9  ........................................ Storeroom & Inventory System *     37

Section 10 ............................................ Emergency / Safety Program *    38

* NOTE: Information in Sections 4 thru 10 is RECOMMENDED for inclusion with

your O&M Manual and Preventive Maintenance Logs, but is not specifically required as part of your

O&M Manual

Upon completion, DO NOT submit your O&M Manual & Preventive Maintenance Logs to the WY DEQ or USEPA. EPA will verify that you have these documents during their Sanitary Survey of your system (routine water system inspection).

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

O&M Manual and Preventive Maintenance Logs

This template has been developed to help you prepare your own O&M Manual and Preventive Maintenance Log.

OPERATION & MAINTENANCE MANUALS

Who: ALL water systems regardless of size

What: Up-To-Date Operation & Maintenance Manual of Your System

When: NOW

Where: Keep a copy in your water plant office and each well house.

Why: To meet USEPA & Wyoming DEQ regulations

The O&M Manual should be a quick reference for successful daily operation

and include anything from trouble shooting to emergency procedures. The

rule requires the O&M Manual to contain:

􀀹 Bound and Indexed Equipment Manufacturer Manuals (you can

download most of these manuals off of the web or get them from

equipment manufacturers)

􀀹 Operation and Control Procedures

􀀹 Preventive Maintenance and Repair Procedures

We recommend that you make at least two copies of the O&M Manual and store one in a safe place in case the plant copy gets lost or damaged by normal use. Your O&M Manual and Preventive Maintenance Logs can be stored in a 3-ring binder.

PREVENTIVE MAINTENANCE LOGS

Who: ALL water systems regardless of size

What: Up-To-Date Preventive Maintenance Logs of Your System

When: NOW

Where: Keep a copy in your water plant office

Why: We recommend that you include the Preventive Maintenance Logs in your 	O&M Manual Binder.

The Preventive Maintenance Logs show the date and type of all maintenance performed on;

􀀹 Preventive Maintenance Logs on Electrical and Mechanical Equipment

􀀹 Cleaning and Inspection Logs of Treatment Facilities and Storage Tanks

􀀹 Records of Coatings and Linings Rehabilitation or Repair

􀀹 Licensed Engineer Inspection Report (once every 5-years) for Finished-	Drinking-Water Storage Tanks and Hydro-pneumatic Tanks

􀀹 Written Flushing Program and Logs showing that Dead-End Water Mains are 	being flushed at least quarterly

􀀹 Isolation Valves Exercise Logs

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 1 – Maintenance Contacts List

This Operations & Maintenance (O&M) Manual is to used as a reference in the overall operation and maintenance of this Water System. This manual contains the necessary O&M procedures, worksheets, and record keeping forms, safety and emergency procedures, and testing and monitoring procedures. This manual is to be updated from time to time to reflect physical and procedural changes to the water system. Also it is intended that this manual be used as a training tool for new employees and as a guide for qualified substitute operators.

Service / Repair Contacts

| Organization | Name & |  |  |  |
| --- | --- | --- | --- | --- |
| or Company | Position | Telephone | Cell Phone | e-mail |
| Water Testing Lab |  |  |  |  |
| Water Testing Lab |  |  |  |  |
| Pump Supplier |  |  |  |  |
| Pump Repair |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Equipment Vendor |  |  |  |  |
| Chemical Supplier |  |  |  |  |
| Chlorine Supplier |  |  |  |  |
| Electrical Contractor |  |  |  |  |
| Wyoming One-Call |  |  |  |  |
| Excavation Contractor |  |  |  |  |
| Consulting Engineer |  |  |  |  |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 2 - Bound and Indexed Equipment

Manufacturer Manuals

Attach ALL Equipment Manufacturer Manuals in this Section.

System Description & Major Equipment (Attach additional sheets if needed)

Source or Sources of Water (Wells, Surface, WY SEO #) _________________________

______________________________________________________________________________

Well Pumps (Size, Mfr & Model)____________________________________________________

Types of Treatment (e.g., Chlorination, Filtration, etc.) ______________________________

____________________________________________________________________________________________________________________________________________________________

Chlorine Feed Equipment (Size, Mfr & Model) _________________________________________

Ammonia Feed Equipment (Size, Mfr & Model) ________________________________________

Ortho/Polyphosphate Feed Pumps (Size, Mfr & Model) __________________________________

Other Chemical Feed Equipment (Size, Mfr & Model) ____________________________________

Treatment Equipment (Size, Mfr & Model) _____________________________________________

Treatment Equipment (Size, Mfr & Model)_____________________________________________

Treatment Equipment (Size, Mfr & Model)_____________________________________________

Standby Power Equipment (Size, Mfr & Model)_________________________________________

Major Controls

Control Valves (Size, Mfr & Model)___________________________________________________

Pump Controls (Type, Mfr & Model)__________________________________________________

Other Controls (Type, Mfr & Model)__________________________________________________

Storage & Distribution Features

High Service Pumps (Size, Mfr & Model)______________________________________________

High Service Pumps (Size, Mfr & Model)______________________________________________

High Service Pumps (Size, Mfr & Model)______________________________________________

Storage Tanks (Size, Mfr & Model)___________________________________________________

Storage Tanks (Size, Mfr & Model)___________________________________________________

Storage Tanks (Size, Mfr & Model)___________________________________________________

We suggest attaching a water treatment plant/groundwater well(s) control schematic and system map / diagram to show system components, including sampling points/taps (SP's or points of collection) which are used for bacteriological and chemical sampling, also see recommended Sections for optional O&M information.

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 3 - Preventive Maintenance Log

It is essential that water system operators provide Preventive Maintenance for protection of the

health and safety of the public; proper equipment operation and preservation; and as required by

the US EPA and WyDEQ. Your water system may be more complex, if so you will need to add additional Preventive Maintenance categories.

The purpose of any maintenance program is: to ensure that equipment is properly functioning; to

maximize system reliability; to ensure that equipment meets or exceeds its expected service life; and to ensure that equipment repairs can be performed in a scheduled manner avoiding the extra costs and disruptions caused by unexpected equipment failure.

There are three kinds of maintenance activities that you will perform. These are predictive, Preventive and breakdown maintenance. PREDICTIVE MAINTENANCE includes such items as oil analysis, to determine optimal oil replacement frequency, infrared analysis, to ensure that electrical connections are sound and that there are no imminent electric failures about to occur and vibration analysis, to ensure that equipment is properly aligned and that bearing wear is identified well before failure occurs.

PREVENTIVE MAINTENANCE is a schedule of planned maintenance actions aimed at the

prevention of breakdowns and failures in water systems. The primary goal of preventive maintenance is to prevent the failure of pumps and equipment before it actually occurs. It is designed to preserve and enhance equipment reliability by replacing worn components before they actually fail. Preventive maintenance activities include exercising valves and fire hydrants; equipment and tank inspections; partial or complete overhauls at regular specified periods; oil changes; lubrication; and so on. In addition, operators can record equipment deterioration so they know to replace or repair worn parts before they cause system failure.

How often should preventive maintenance for equipment be performed?

A. Once every week

B. After a breakdown

C. According to manufacturer recommendations

D. When time permits

E. According to a well thought out plan

F. Just before a Sanitary Survey

The answer is both C and E. The ideal preventive maintenance program would prevent all water

system equipment failure before it occurs. Long-term benefits of preventive maintenance include:

improved system reliability, decreased cost of replacement, decreased system downtime, and better spares inventory management.

BREAKDOWN MAINTENANCE is maintenance that must be performed because of unexpected

equipment failure. This is the most disruptive and costly type of maintenance and the purpose of a good maintenance program is to minimize these unscheduled events. There are multiple

misconceptions about the benefits of preventive maintenance. One such misconception is that

preventive maintenance is unduly costly, time consuming, or causes disproportionate work. This logic dictates that it would cost more for regularly scheduled downtime and maintenance than it would normally cost to operate equipment until failure or repair is absolutely necessary. This may be true for some smaller equipment components; however, one should compare not only the costs but also the long-term benefits and savings associated with preventive maintenance. Without a sound preventive maintenance program, labor costs for lost water production time from unscheduled equipment breakdown will be incurred, damages to equipment can be much more severe and potential negative treatment process and/or regulatory ramifications can be unacceptable to the customer and costly to the system.

Even under the best Preventive maintenance program, some breakdown maintenance will occur.

Each of these events provides a learning opportunity to improve upon existing Preventive

maintenance programs. The operator should evaluate every equipment breakdown situation, to

determine the cause, and what measures could have been taken to prevent the occurrence. The

lessons learned should then be added to the Preventive maintenance program. Building these written feedback loops into the Preventive maintenance program will yield significant returns.

Other Maintenance Items ~ Recommended charts can be very helpful in designing or in improving an existing Preventive maintenance system, Water Systems are advised to use these to develop customized maintenance information documentation for operators and maintenance personnel that are specific to their systems. General maintenance is imperative in keeping a plant in working condition. The following items should be included;

􀀹 Preventive maintenance schedule and instructions for completion;

􀀹 List of Specifications for fuels, lubricants, filters, etc. for equipment;

􀀹 Trouble shooting charts or guides which references pages in O&M manual and manufactures

O&M manual;

􀀹 Record system for each type of equipment, this should include; numbering system, catalog,

nameplate data cards, maintenance record cards;

􀀹 Manufacturers’ maintenance schedule for routine adjustments. A summary with references to

page number in manufacturer’s O&M manual needs to be provided;

􀀹 A work order system for maintenance of equipment with sample forms.

􀀹 A designated responsible individual to ensure that the program tasks are being met and that

timely updates are included in the program as needed

􀀹 Lastly, another benefit of a sound Preventive maintenance program is the ability to identify

maintenance trends that consume a great deal of the operator’s time. In these cases 	these trends provide the documentation necessary to management for replacement of 	equipment that is not performing in an acceptable manner. A Preventive maintenance 	program that is used in this way can achieve significant cost reductions, improve system 	reliability, and provide the operator with more time to devote to more critical tasks.

TYPICAL DUTIES OF A WATER PLANT OPERATOR

1. Start up, shut down, and make periodic operating checks of plant equipment, such as pumping systems, chemical feeders, auxiliary equipment (compressors), and measuring and control systems.

2. Perform routine Preventive maintenance, such as lubrication, operating adjustments, cleaning and painting equipment.

3. Load and unload chemicals, such as chlorine cylinders, bulk liquids, powdered chemicals, and bagged chemicals either by hand or using chemical handling equipment such as forklifts and hoists.

4. Perform minor corrective maintenance on plant mechanical equipment; for example, chemical feed pumps and small units.

5. Maintain plant records, including operating logs, daily diaries, chemical inventories, and data logs.

6. Monitor the status of plant operating guidelines, such as flows, pressures, chemical feeds, levels, and water quality indicators, by reference to measuring systems.

7. Collect representative samples and perform laboratory tests on samples for turbidity, color, odor, coliforms, chlorine residual, and other tests as required.

8. Order chemicals, repair parts and use tools.

9. Estimate and justify budget needs for equipment and supplies.

10. Conduct safety inspections, follow safety rules for plant operations, and also develop and conduct tailgate safety meetings.

11. Discuss water quality with the public, conduct tours of your plant (especially for school children), and participate in your employer’s public relations program.

12. Communicate effectively with other operators and supervisors on the technical level expected for your position.

13. Make arithmetic calculations to determine chemical feed rates, flow quantities, detention and contact times, and hydraulic loadings as required for plant operations

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Recommended Daily Operational Duties / Preventive Maintenance

(check or circle items that apply ~ strikethrough items that do NOT apply)

Water Production Meter Readings

􀂉 Record Water Plant Meter Readings

􀂉 Calculate Total Daily Production

Pumps & Tank Levels

􀂉 Inspect Well Pumps & Controls

􀂉 Check Chemical Solution Tanks & Record Amount Used

􀂉 Check & Record Water Levels in Storage Tanks

􀂉 Inspect Chemical Feed Pumps

􀂉 Inspect High Service Pumps & Controls

􀂉 Record Pump Run Times & Start Cycles

Sampling & Readings

􀂉 Check & Record Chlorine Residual at Point of Application

􀂉 Check & Record Chlorine Residual at Nearest Customer (Systems Req’d to Provide CT)

􀂉 Check & Record Chlorine Residual in Distribution System at Remote Points

􀂉 Check Instrumentation for Proper Input / Output

Security

􀂉 Investigate Customer Complaints

􀂉 Complete a Daily Security Check

􀀹 Windows, Doors, Hatches, Vents, Screens for Evidence of Tampering or Vandalism

􀀹 Well Caps, Vents & Seals

􀀹 Security Lighting, Locks & Alarms

􀀹 Inspect Fences & Gates

Recommended Weekly Operational Duties / Preventive Maintenance

(check / circle items that apply ~ strikethrough items that do NOT apply)

Inspections & Conditions

􀂉 Inspect Chlorine & Fluoride Testing Equipment (Calibration & Reagents)

􀂉 Check & Record Well Pumps Pumping Rate

􀂉 Check Membrane System Pressure Differential

Cleaning

􀂉 Clean Pump House and/or Plant Operations Office

􀂉 Clean Water System Grounds

Security

􀂉 Check ALL Station Alarms for Proper Operation

􀂉 Check Stand-By Power Source to Ensure Emergency Operation

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Recommended Monthly Operational Duties / Preventive Maintenance

(check or circle items that apply ~ strikethrough items that do NOT apply)

Inspections & Conditions

􀂉 Check & Record Electric Meters

􀂉 Take Appropriate Monthly Water Quality Samples

􀂉 Check & Record Static & Draw-Down (Pumping) Levels in Wells

􀂉 Confirm Submittal of Monthly Operation Reports (MORs)

􀂉 Lubricate Pumps, Motors, Blowers & ALL Moving/Rotating Equipment

􀂉 Inspect ALL Pumps House Water Lines, Gaskets & Fittings for Corrosion & Leaks

􀂉 Inspect Pump, Seals, Water Lines & Fittings for Corrosion & Leaks

􀂉 Listen to Pump for Unusual Noises (or signs that Bearings are Wearing Out)

􀂉 Inspect Scales, Analyzer / Alarm, Oxygen Breathing Apparatus, Cross Ventilation

􀂉 Inspect Filter Head for Leaks

􀂉 Inspect and Add Salt to Brine Tank (i.e. Ion Exchange Only)

􀂉 Run Emergency Generator for 30-min UNDER LOAD, Check ALL Fluid and Fuel Levels

􀂉 Test Eye Wash & Emergency Shower

Cleaning

􀂉 Inspect, Clean & Disinfect Wellheads

􀂉 Inspect & Clean Chlorine Injection Points

Security

􀂉 Inspect Tank Overflow Vent Screens, Ensure Screen Intact, Check Manway Hatch & Ensure it

is Secured

Recommended Quarterly Operational Duties / Preventive Maintenance

(check or circle items that apply ~ strikethrough items that do NOT apply)

Cleaning

􀂉 Flush Dead-End Lines (Feb, May, Aug & Nov)  more often per your written flushing program *

􀂉 Lubricate Locks

􀂉 Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

* Note: Flushing of dead-end water mains may be limited to just those dead-end mains that are 6 inches or greater in diameter if there is no history of water quality problems at dead-end mains smaller than 6 inches in diameter.

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Preventive Maintenance (PM) Recommendations

January PM Recommendations (Non - Peak Month)

(check items apply ~ strikethrough items that do NOT apply)

􀂉 Contact Electrician to Check Emergency Generator & Run on Load Bank

􀂉 Contact Electrician to Check Running Amps on Pumps

􀂉 Make Sure Unnecessary Equipment is Properly Decommissioned

􀂉 Review Emergency Response Plan – Update as Necessary

􀂉 Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

February PM Recommendations (Non - Peak Month)

(check items apply ~ strikethrough items that do NOT)

􀂉 Prepare Water System for Summer Operation / Hurricane Season (Fuel, Generators, Shutters)

􀂉 Building Preventive Maintenance

March PM Recommendations (Non - Peak Month) (check items apply ~ strikethrough items that do NOT apply)

􀂉 Inspect Storage Tanks for Defects & Sanitary Deficiencies

􀂉 Clean Storage Tanks as Needed

􀂉 Structural Inspection of Tank & Coatings by Engineer at Least Every 5-yrs and Before Aug 2008 (Clean Tank Prior)

􀂉 Perform Tank Coating Repairs per Mfr Specifications & Recommendations

􀂉 Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

April PM Recommendations

(check items apply ~ strikethrough items that do NOT apply)

􀂉 Clean & Inspect Chemical Feed Lines

􀂉 Clean & Inspect Chemical Solution Tank

􀂉 Calibrate Chemical Feed Pumps

􀂉 Repair non-working FH & valves found during flushing & exercising program

May PM Recommendations (Peak Month)

(check items apply ~ strikethrough items that do NOT)

􀂉 Repair non-working Fire Hydrants & Valves (found during flushing & exercising program)

􀂉 Water Plant & Pump House Building Preventive Maintenance

􀂉 Flush Dead-End Lines (Feb, May, Aug & Nov) Required by FDEP Rule 62-555.350(2) or more 	often

June PM Recommendations (Peak Month)

(check items apply ~ strikethrough items that do NOT)

􀂉 Flush HALF Distribution System

􀂉 Exercise HALF of ALL Fire Hydrants

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

July PM Recommendations (Peak Month)

(check items apply ~ strikethrough items that do NOT apply)

􀂉 Flush Remaining Distribution System (not completed in January)

􀂉 Exercise Remaining Fire Hydrants (not completed in January)

􀂉 Flush Dead-End Lines (Feb, May, Aug & Nov) or more often

􀂉 Inspect, Clean & Repair Control Panels in Water Treatment Plant

August PM Recommendations (Peak Month)

(check items apply ~ strikethrough items that do NOT apply)

􀂉 Operate ALL Valves Inside Treatment Plant & Pump House

􀂉 Clean & Inspect ALL Safety Equipment

􀂉 Flush Dead-End Lines (Feb, May, Aug & Nov)

September PM Recommendations

(check items apply ~ strikethrough items that do NOT apply)

􀂉 Clean RO Membranes or per Mfr Recommendations

􀂉 Test Pressure Reducing Valves & RPZs

􀂉 Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

􀂉 Inspect Pressure Relief Valves on Hydropneumatic Tanks

􀂉 Inspect Air Compressor on Hydropneumatic Tanks

􀂉 Overhaul or Replace Pressure Relief Valves on Hydropneumatic Tanks – every 5-yrs or per Mfr Recommendations

October PM Recommendations

(check items apply ~ strikethrough items that do NOT apply)

􀂉 Overhaul Chemical Feed Pumps

(Feeder Head Cleaned, O-Rings, Check Valves & Diaphragms, Worn-Out Parts Replaced)

􀂉 Clean & Inspect Chemical Feed Lines & Solution Tanks

􀂉 Calibrate Chemical Feed Pumps after Overhaul

􀂉 Test Eye Wash & Emergency Shower

November PM Recommendations

(check items apply ~ strikethrough items that do NOT apply)

􀂉 Exercise HALF of ALL Mainline Valves (You may consider combining Valve Exercising with your Flushing & FH Exercising Program if this is appropriate for your system)

􀂉 Check Water Meter For Accuracy (2" or Less Every 3-yrs Recommended) or Annually per Mfr Recommendations

􀂉 Change Media in Filter or per Mfr Recommendations

􀂉 Flush Dead-End Lines (Feb, May, Aug & Nov)

December PM Recommendations

(check items apply ~ strikethrough items that do NOT)

􀂉 Exercise Remaining HALF of ALL Mainline Valves (not exercised in November)

􀂉 ALL Safety Equipment - Clean & Inspect

􀂉 Clean, Inspect & Disinfect Aerator / Degassifier Screens, Sprayheads & Gaskets

􀂉 Clean, Inspect & Disinfect Aerator / Degassifier

Suggested Preventative Maintenance Logs

Your water System may be more complex, if so you will need to add categories. (Strike through items that do NOT apply)

|  |  | Last |  |  |
| --- | --- | --- | --- | --- |
| Category Suggested | Frequency | Service | Service | Service |
|  |  | (Date) | (Date) | (Date) |
| Well / Source Water |  |  |  |  |
| Clean & Inspect Wellheads, Pump, |  |  |  |  |
| Controls Seals, Vent & Screen | Monthly |  |  |  |
| Check & Record Static & Draw-Down |  |  |  |  |
| (Pumping) Levels in Wells | Monthly |  |  |  |
| Water Plant & Pump House |  |  |  |  |
| Inspect Water Lines, Gaskets & Fittings |  |  |  |  |
| for Corrosion & Leaks | Monthly |  |  |  |
| Lubricate Pumps, Motors, Blowers and |  |  |  |  |
| ALL Moving / Rotating Equipment | Monthly |  |  |  |
| Building Preventive Maintenance | Annually - July |  |  |  |
| Exercise ALL Valves Inside Treatment |  |  |  |  |
| Plant & Pump House (AWWA M44 once 2-yrs) | Annually - August |  |  |  |
| Check Water Meter For Accuracy (2" or | Every 3 yrs - Nov |  |  |  |
| Less Every 3-yrs Recommended) | (or per Mfr) |  |  |  |
| High Service Pumps |  |  |  |  |
| Inspect Pump, Seals, Water Lines & |  |  |  |  |
| Fittings for Corrosion & Leaks | Monthly |  |  |  |
| Listen to Pump for Unusual Noises (or |  |  |  |  |
| signs that Bearings are Wearing Out) | Monthly |  |  |  |
| Safety & Security |  |  |  |  |
| ALL Safety Equipment - Clean & Inspect |  |  |  |  |
| (Lock Out Tags) | Annually - Dec |  |  |  |
| Emergency Response Plan |  |  |  |  |
| Review/Update | Annually - June |  |  |  |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Suggested Preventative Maintenance Logs

Your water System may be more complex, if so you will need to add categories. (Strike through items that do NOT apply)

| Chemical Feed Systems (Liquid) |  |  |  |  |
| --- | --- | --- | --- | --- |
| Inspect Pump, Seals, Water Lines & |  |  |  |  |
| Fittings for Corrosion & Leaks | Monthly |  |  |  |
| Clean Chlorine Injection Points | Monthly |  |  |  |
| Overhaul Chemical Feed Pumps (Feeder |  |  |  |  |
| Head Cleaned, O-Rings, Check Valves & | Annually - Oct |  |  |  |
| Diaphragms, Worn-Out Parts Replaced) |  |  |  |  |
| Test Eye Wash & Emergency Shower | 2xYR - Apr & Oct |  |  |  |
| Chemical Feed Lines - Clean & Inspect | 2xYR - Apr & Oct |  |  |  |
| Chem Solution Tanks - Clean & Inspect | 2xYR - Apr & Oct |  |  |  |
| Calibrate Chemical Feed Pumps | 2xYR - Apr & Oct |  |  |  |
| Chemical Feed Systems (Gas) |  |  |  |  |
| Inspect Scales, Analyzer / Alarm, Oxygen |  |  |  |  |
| Breathing Apparatus, Cross Ventilation | Monthly |  |  |  |
| Inspect & Clean Chlorine Injection Points | Monthly |  |  |  |
| Aerator / Degassifer |  |  |  |  |
| Inspect Screens, Sprayheads & Gasket | Annually - Dec |  |  |  |
| Clean, Inspect & Disinfect Aerator / |  |  |  |  |
| Degassifer | Annually - Dec |  |  |  |
| Filter / Water Softner |  |  |  |  |
| Inspect Filter Head for Leaks | Monthly |  |  |  |
| Inspect and Add Salt to Brine Tank (i.e. |  |  |  |  |
| Ion Exchange Only) | Monthly |  |  |  |
| Change Media in Filter | per Mfr - Nov |  |  |  |
| Reverse Osmosis / Membrane Softening Unit |  |  |  |
| Check Pressure Differential | Weekly |  |  |  |
| Clean Membranes | per Mfr |  |  |  |
| Replace Membranes | per Mfr |  |  |  |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Suggested Preventative Maintenance Logs

Your water System may be more complex, if so you will need to add categories. (Strike through items that do NOT apply)

|  |  | Last |  |  |
| --- | --- | --- | --- | --- |
| Category Suggested | Frequency | Service | Service | Service |
|  |  | (Date) | (Date) | (Date) |
| Storage Tanks – attach Inspection Reports with Preventive maintenance plan |  |
| Inspect Overflow Vent Screens, Ensure |  |  |  |  |
| Screen Intact, Check Manway Hatch & | Monthly |  |  |  |
| Ensure it is Secured |  |  |  |  |
| Inspect Storage Tanks for Defects, Leaks |  |  |  |  |
| & Sanitary Deficiencies | Annually - Mar |  |  |  |
| Clean Storage Tanks if Needed | Annually - Nov |  |  |  |
| Structural Inspection of Tank & Coatings | Every 5 YRS |  |  |  |
| by Engineer (Clean Prior to Inspection) | March or Nov |  |  |  |
| Perform Coating Repairs per Mfr Specs | Annually - April |  |  |  |
| Inspect Hydro Tank PRV & Compressor | Annually - Sept |  |  |  |
| Replace Hydro Tank PRV | Every 5 YRS |  |  |  |
| Controls, Electrical & Stand-By Power |  |  |  |  |
| Inspect, Clean & Repair Control Panels in | Annually - Feb |  |  |  |
| Water Treatment Plant |  |  |  |  |
| Prepare Water System for Summer |  |  |  |  |
| Operation | Annually - Mar |  |  |  |
| Run Generator 30-min Under Load | Monthly |  |  |  |
| Contact Electrician to Check Emergency |  |  |  |  |
| Generator & Run on Load Bank | Annually - June |  |  |  |
| Contact Electrician to Check Running |  |  |  |  |
| Amps on Pumps | Annually - June |  |  |  |
| Distribution System |  |  |  |  |
| (You may consider combining Exercising and Flushing Programs if this is appropriate for your system) * |
| Exercise ALL Mainline Valves | Annually - Fall | See Chart | on Next | Page |
| Flush Distribution System & |  |  |  |  |
| Exercise ALL Fire Hydrants | Annually - Apr | See Chart | on Next | Page |
| Flush Dead-End Lines | Quarterly - Feb |  |  |  |
|  | May, Aug & Nov | See Chart | on Next | Page |
| Repair Non-Working Valves & Fire |  |  |  |  |
| Hydrants (found during exercising and | As found | See Chart | on Next | Page |
| flushing) |  |  |  |  |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Suggested Preventive Maintenance Log (continued)

| Exercise ALL Mainline Valves - Annually Jan & Feb (add sheets as needed) |
| --- |
| Valve |  | Last |  |  |  |
| ID # | Valve Location | Service | Service | Service | Service |
|  |  | (date) | (date) | (date) | (date) |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Suggested Preventive Maintenance Log (continued)

| Exercise ALL Fire Hydrants - Annually Oct - Nov (add sheets as needed) |  |
| --- | --- |
| Hydrant |  | Last |  |  |  |
| ID # | Fire Hydrant Location | Service | Service | Service | Service |
|  |  | (date) | (date) | (date) | (date) |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Suggested Preventive Maintenance Log (continued)

| Flush Distribution System - Annually Nov & Dec (add sheets as needed) |
| --- |
| Pipe |  | Last |  |  |  |
| ID # | Pipe Segment Location | Service | Service | Service | Service |
|  |  | (date) | (date) | (date) | (date) |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

EXAMPLE VALVE RECORD

Location (street / address):_______________________________________________________

Type:___________________________ Make:__________________________ Size:__________

Opens: 􀂆 Left 􀂆 Right 􀂆 Other:__________________________________ # of Turns:_______

Date Installed:_____________________________

| Date | Closes/Opens? | # of |  | Valve Status |
| --- | --- | --- | --- | --- |
| Exercised | (Y / N) | Turns | Condition of Stem, Packing, Nut, Gearing | (Open or Closed) |

EXAMPLE DEAD-END WATER MAIN FLUSHING RECORD

Location (street):

|  | Flushing | Water Characteristics | Disinfectant Residual, mg/L |
| --- | --- | --- | --- |
| Flushing | Duration | (color, odor, etc.) |  |  |
| Date | (min.) | Before Flushing | After Flushing | Before Flushing | After Flushing |

Section 4 – Emergency Response Plan

This information in Appendices A thru G is RECOMMENDED for inclusion with your O&M Manual and Preventive Maintenance Logs, but is not specifically required.

.

Insert your ERP here.

WARWS can help: We encourage you to use the National Rural Water / Wyoming Rural Water Association’s Emergency Response Plan (ERP) templates and guides off our website. WARWS is ready to help you complete your ERP. Please call our office, Circuit Riders or Source Water Protection staff for assistance.

An abbreviated Emergency Response Plan template has been included (pages 21 thru 32).

This ERP is intended as a quick reference for most systems. A full Vulnerability Assessment and Emergency Response plan should still be done.

Do Not include anything classified in this plan. If it’s not something you would want available to the public, don’t put it in here.

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Emergency Response Plan

Abbreviated Vulnerability Assessment & Emergency Response Plan for Smaller Public Water Systems

9/1/2010

Prepared by Wyoming Association of Rural Water Systems

PO Box 1750

Glenrock, WY 82637

307-436-8636

warws@warws.com

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

System Identification

System Information

| Water Station ID | WY56 |
| --- | --- |
| Water Station Name |  |
| Town/City |  |

Telephone and Contact Information

| Contact Name |  |
| --- | --- |
| Daytime Phone |  |
| Emergency Phone |  |
| Cell Phone |  |
| Fax Number |  |
| Emergency Email |  |

Other Information

| Population Served |  |
| --- | --- |
| Num of Srv. Conns. |  |
| System Owner |  |

Person Responsible for Emergency Maintaining Contact List

| Name |  |
| --- | --- |
| Title |  |
| Telephone |  |

Internal Chain of Command

| 1st Person to Contact |  |
| --- | --- |
| 2nd Person to Contact |  |
| 3rd Person to Contact |  |
| 4th Person to Contact |  |

External Chain of Command

| 1st Person to Contact |  |
| --- | --- |
| 2nd Person to Contact |  |
| 3rd Person to Contact |  |
| 4th Person to Contact |  |

Security Assessment

- Are all critical facilities fenced, including well houses, and pump pits, and are gates locked when appropriate?

- Are warning signs (tampering, unauthorized access, etc.) posted on all critical components of your water system? (For example, well houses, storage tanks, etc.)

- Do you have a neighborhood watch program for your water system?

- Are your wellheads sealed properly?

- Are well vents and caps screened and securely attached?

- Are observation, test, and abandoned wells properly secured to prevent tampering?

- Is your surface water source secured with fences or gates?  Do water system personnel visit the source?

- Are chemicals, particularly those that are potentially hazardous (e.g. chlorine gas) or flammable, properly stored in a secure area?

- Are tank ladders, access hatches, and entry points secured?

- Are vents and overflow pipes properly protected with screens and/or grates?

- Can you isolate the storage tank from the rest of the system?

- Do you control the use of hydrants and valves?

- Has your system implemented a backflow prevention program?

- When hiring personnel, do you request that local police perform a criminal background check, and do you verify employment eligibility (as required by the Immigration and Naturalization Service, Form I-9)?

- When terminating employment, do you require employees to turn in photo IDs, keys, access codes, and other security-related items?

- If you have a web-site, have you removed all information that can be used to disrupt your system or contaminate your water?

- Do you have a procedure in place to receive notification of a suspect outbreak of a disease immediately after discovery by local health agencies?

- Do you have a procedure in place to advise the community of contamination immediately after discovery?

Coordination

- Have you contacted the local police department?

- Have you contacted the local health department?

- Have you contacted the local fire department?

- Have you contacted the local emergency medical responders?

- Have you contacted your State Rural Water Association?

- Have you contacted the FBI Field Office in your area?

- Have you contacted your locally elected official?

- Have you ensured that all of the above have communicated and know their responsibilities in the event of an emergency?

- Have you trained the water system staff on their roles and responsibilities in the event of an emergency?

- Do you have a plan to notify your customers of any “Boil Water” or “Do Not Use” notices?

Describe your customer notification plan-

______________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________________

Critical Equipment

Source Water Type

| Source | Name/Identification | Description/Location |
| --- | --- | --- |
| Ground Water |  |  |
| Surface Water |  |  |
| Purchased Water |  |  |

Treatment Plant/ Ground Water Wells

| Plants | Name/Identification | Description/Location |
| --- | --- | --- |
| Buildings |  |  |
| Pumps |  |  |
| Treatment Equipment |  |  |
| Process Controls |  |  |
| Chemicals and Storage |  |  |
| Lab Chemicals |  |  |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Storage Tanks

| Tanks | Name/Identification | Description/Location |
| --- | --- | --- |
| Storage Tanks |  |  |
| Pressure Tanks |  |  |

Power

| Power | Name/Identification | Description/Location |
| --- | --- | --- |
| Primary |  |  |
| Auxiliary |  |  |

Distribution Systems

| Distribution | Name/Identification | Description/Location |
| --- | --- | --- |
| Pumps |  |  |
| Pipes |  |  |
| Valves |  |  |
| Appurtenances (e.g. flush valves) |  |  |
| Other Vulnerable Points |  |  |

Offices

| Offices | Name/Identification | Description/Location |
| --- | --- | --- |
| Buildings |  |  |
| Computers |  |  |
| Files |  |  |
| Transportation Work Vehicles |  |  |

Communications

| Communications | Name/Identification | Description/Location |
| --- | --- | --- |
| Cell Phones |  |  |
| Radio |  |  |
| Telephones |  |  |
| Computer Control Systems |  |  |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Notification/Contact Information

| Organization | Contact Name/Title | Phone (Day) | Phone (Night) | Email |
| --- | --- | --- | --- | --- |
| Fire Department |  |  |  |  |
| Police Department |  |  |  |  |
| Emergency Medical Service |  |  |  |  |
| Local Health Department |  |  |  |  |
| National Spill Response Center |  |  |  |  |
| State Spill Hotline |  |  |  |  |
| Local/Regional Laboratory |  |  |  |  |
| Water System Operators |  |  |  |  |

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Local Notification

| Organization | Contact Name/Title | Phone (Day) | Phone (Night) | Email |
| --- | --- | --- | --- | --- |
| Government Officials |  |  |  |  |
| Emergency Planning Committee |  |  |  |  |
| Hospitals |  |  |  |  |
| Pharmacy |  |  |  |  |
| Nursing Homes |  |  |  |  |
| Schools |  |  |  |  |
| Local/Regional Laboratory |  |  |  |  |
| Water System Operators |  |  |  |  |

Service/Repair Notification

| Organization | Contact Name/Title | Phone (Day) | Phone (Night) | Email |
| --- | --- | --- | --- | --- |
| Electrician |  |  |  |  |
| Electric Utility Company |  |  |  |  |
| Gas Utility Company |  |  |  |  |
| Sewer Utility Company |  |  |  |  |
| Telephone Utility Company |  |  |  |  |
| Plumber |  |  |  |  |
| Pump Specialist |  |  |  |  |
| “Dig Safe” or Local Equivalent |  | 811 |  |  |
| Soil Excavator/Backhoe Operator |  |  |  |  |
| Power Generator Rentals |  |  |  |  |
| Chlorinator Rentals |  |  |  |  |
| Portable Fencing Rentals |  |  |  |  |
| Equipment Repairmen |  |  |  |  |
| Chlorinator Repairmen |  |  |  |  |
| Radio/Telemetry Repair Service |  |  |  |  |
| Bottled Water Service |  |  |  |  |
| Bulk Water Hauler |  |  |  |  |
| Pump Supplier |  |  |  |  |
| Well Driller |  |  |  |  |
| Pipe Supplier |  |  |  |  |
| Chemical Supplier |  |  |  |  |

State Notification

| Organization | Contact Name/Title | Phone (Day) | Phone (Night) | Email |
| --- | --- | --- | --- | --- |
| Dept. of Env. Protection | Tiffany Mifflin Alysia Tien | 303-312-6521 303-312-7021 | 800-424-8802 Water Security |  |
| Department of Health | Angela Benhouten | 307-777-7656 | 888-996-9104 |  |
| Emergency Mgmt. Agency | DEQ Homeland Security | 307-777-5885 307-777-4663 | 307-777-7781 307-777-4900 |  |

Media Notification

| Organization | Contact Name/Title | Phone (Day) | Phone (Night) | Email |
| --- | --- | --- | --- | --- |
| Water System Spokesperson |  |  |  |  |
| Newspaper-Local |  |  |  |  |
| Newspaper-Regional/State |  |  |  |  |
| Radio |  |  |  |  |
| Television |  |  |  |  |

Other Notification

| Organization | Contact Name/Title | Phone (Day) | Phone (Night) | Email |
| --- | --- | --- | --- | --- |

Employees

| Title | Name | Phone (Day) | Phone (Night) | Email |
| --- | --- | --- | --- | --- |

Alternative Water Sources

- Bottle:

- Bulk:

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 5 – Permits & Specific Conditions

This information in Appendices A thru G is RECOMMENDED by WARWS for inclusion with your O&M Manual and Preventive Maintenance Logs, but is not specifically required.

Insert PERMITS and SPECIFIC CONDITIONS for your

Water System here.

Include any US EPA and WyDEQ provisions for your water system plus any applicable rules, regulations, latest Sanitary Survey, Well Logs (certification of completion), SEO water right permits & documents.

Use this section to reference Quarterly, Bi-Yearly and Yearly reporting requirements specific to your system to State and Federal Agencies.

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 6 – System Description & Reports

.This information in Appendices A thru G is RECOMMENDED by WARWS for inclusion with your O&M Manual and Preventive Maintenance Logs, but is not specifically required.

A General System Description should include:

􀀹 Description of Treatment Processes

􀀹 Principal Design Criteria and Process Equipment Ratings

􀀹 Water System Map indicating Major Valves and Water Storage Tanks

􀀹 Process Flow Schematic Water Treatment System

􀀹 Brief Description of Interconnections

􀀹 Mutual Aid Agreements with Adjacent Water Systems / WYWARN

Records and Reports. Keeping and compiling records is a valuable part of an efficient water system.

The following should be included in the manual:

􀀹 A general explanation of the importance of records & reports;

􀀹 The system should maintain a list of complaints and identify responses made;

􀀹 Daily logs, maintenance records, laboratory records, monthly reports, monitoring reports,

annual reports, operating cost reports, accident reports, and sanitary surveys. Examples and

sample reports of each should be included;

􀀹 A listing of records that are on file (permits and standards, consumption);

􀀹 Location of records on file;

􀀹 Procedures for reporting records to appropriate agencies;

􀀹 Specify how long records should be kept on file;

Water Treatment Plant As-Builts, Equipment Manuals and Vendor Catalogues. Maintaining a

current set of plant drawings, equipment manuals and vendor catalogues is critical in promoting timely

repairs and reduces the chances for accidental equipment damage. The following should be provided:

􀀹 As-Builts of all Plant piping and valving and a method for updating the information

􀀹 A centralized storage area that is accessible by those needing the information should be made

available in the plant.

􀀹 Plant equipment manuals should be maintained in a visible and accessible location

􀀹 Current vendor supply catalogues

WARWS can help: We are ready to help you complete your O&M Manual, please our office or contact your Water Circuit Rider for assistance.

Section 7 – General System Operation & Control

This information in Appendices A thru G is RECOMMENDED by WARWS for inclusion with your O&M Manual and Preventive Maintenance Logs, but is not specifically required.

A general System Operation and Control. It is important to fully understand how the water system operates. This section should include;

A. Identification of Major System Components including a description of the normal operation of the component. Show the relationship of each component with other system components, and relate any possible alternative operation modes and circumstances under which they would be used. Include schematic diagrams of each unit and discuss any special features that may be of importance.

B. Preventive Maintenance Program; describe for each major component the Preventive maintenance tasks (if any) that are performed. This should include types of Preventive maintenance or inspection required; frequency of maintenance or inspection; and any extraordinary changes to operations which would occur when a facility is off-line.

C. Common Operating Problems should be discussed along with methods of bypassing units, and the importance of and how to use laboratory tests for unit control.

D. Routine System Operation; for each major system component describe the routine operational tasks that are performed and controlled. This should include start-up and shut down procedures, safety procedures, meter reading and how system performance is evaluated.

E. Special Task Lists. These lists should identify assignments to personnel for notifying regulatory agencies, the media, institutional customers such as hospitals, government buildings or schools and special needs customers who require a continuous supply of water. The list should also include who is authorized as a spokesperson to represent the water system.

F. Staff Contact and Capability Lists. This should include a list staff, emergency contact and listing of any training or ability to perform specialized tasks such as electrical work, welding, operation of CDL vehicles or construction equipment, test equipment, or specialized knowledge in maintenance or operational activities through training, licensing or experience.

WARWS can help: We are ready to help you complete your O&M Manual, please call our office or contact your Water Circuit Rider for assistance.

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 8 – Laboratory Testing

This information in Appendices A thru G is RECOMMENDED by WARWS for inclusion with your O&M Manual and Preventive Maintenance Logs, but is not specifically required.

A general Laboratory Testing.

This should include any samples and tests needed for compliance as well as for process control. For samples taken and analyzed by the system or the State;

􀂃 Type of sample

􀂃 Sampling locations;

􀂃 Monitoring schedule;

or taken by the system and analyzed by an EPA approved laboratory;

􀂃 Name of the laboratory

􀂃 Contact person

􀂃 Telephone number

􀂃 Type of sample

􀂃 Sampling locations;

􀂃 Monitoring schedule;

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 9 – Storeroom & Inventory System

This information in Appendices A thru G is RECOMMENDED by WARWS for inclusion with your O&M Manual and Preventive Maintenance Logs, but is not specifically required.

Having the proper equipment, tools, parts and consumable supplies is critical in maintaining the treatment process and plant equipment operation. Equipment owned by the system should be maintained in good working order and should be available to the employees who may need it for use at all times. Similarly, stocks of spare parts, special tools, supplies, chemicals, and other consumable items should be maintained in a secure storage location with controlled access. An inventory tracking and reorder system that identifies who has used the equipment and consumable parts must be maintained so that acceptable levels of inventory are available when needed and restocked to facilitate timely actions. Minimum FRWA recommendations for managing plant inventory are listed

below:

􀂃 Plant Property, Rolling Stock (vehicles, tractors, construction equipment and trailers), and

Assigned Equipment and Furniture

􀂃 An inventory of all property and equipment, both moveable and non-moveable, owned by

the system;

􀂃 A mechanism for assigning specific items of moveable equipment to individual employees

(e.g. vehicles, tools, etc.)

􀂃 A mechanism for tracking specific items of moveable equipment by location (e.g. furniture,

office equipment, etc.)

􀂃 A mechanism for storage and checking out of specialized items of equipment needed

infrequently.

􀂃 Brief operation instructions for each item of equipment with reference to the manufacturers’

technical specifications for major system components;

􀂃 List of warranted equipment and the warranty provisions;

􀂃 List of outside contract maintenance tasks;

􀂃 List of equipment manufacturers and local suppliers;

􀂃 Spare Parts and Specialized Tools list;

􀂃 Special tools list and tools displayed prominently

􀂃 Spare Parts Inventory, number available and reorder quantity

􀂃 Lists of special test equipment and operating manuals

􀂃 List of major suppliers with telephone numbers and contact persons;

􀂃 A system of requisitions and/or work orders used to distribute parts, supplies, chemicals,

etc. to employees.

􀂃 Lists of equipment and spare parts should clearly indicate those items of equipment and

parts that are essential to the operation of the system.

􀂃 List, number and types of valves, reducers, pipe and repair fittings that are on-hand;

􀂃 Hand Tools, raingear, and miscellaneous hardware used in the plant

Chemicals and Other Consumable Items

􀂃 Recommended stock levels of supplies and chemicals and method of reordering when

stock on hand drops below recommended levels;

􀂃 Delivery dates and critical chemicals such as chlorine, lime, polymers, etc

􀂃 Laboratory Supplies and reorder quantities (generally maintained by the Lab)

􀂃 Identification of responsible party for maintaining of critical inventories

􀂃 List of major suppliers with telephone numbers and contact persons

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.

Section 10 – Emergency / Safety Program

This information in Appendices A thru G is RECOMMENDED by WARWS for inclusion with your O&M Manual and Preventive Maintenance Logs, but is not specifically required.

Emergency / Safety Program

A. An Operating Plan For Emergencies and the procedures to be followed until normal

operation can be resumed. This plan should include personnel assignments, emergency

equipment inventory, and emergency numbers. Phone numbers to keep readily accessible

should be police and fire departments, and for chemical spills or exposure CHEMTECH 800

424-9300. The emergency call up list should identify, in ranked order, water system personnel

responsible for making decisions in specific situations. This list should include the job title,

home and work phone number (beeper/car phone number if available) for all personnel.

B. A Contingency Plan should also be made to insure proper treatment of water even in adverse

conditions. This plan should describe conditions and procedures for putting standby and

emergency sources into active service. Procedures for notifying customers, the local health

jurisdiction, and DEP of noticeable water quality problems. Sample Public Notices should be

prepared for acute Tier I violations and water borne disease outbreaks that must be distributed

within 24-hours.

C. Safety Procedures should identify work space hazards for the waste water system. Potential

hazards include asbestos coated pipes, mechanical equipment, electrical, explosion and fire,

chlorine, oxygen deficiency, laboratory and any chemicals used by the plant. A potential

danger at plants can stem from the chlorination process. The manual should provide

information on how to do the following tasks;

1. Handling of Chlorine Containers.

a. Forklift trucks or hoisting equipment with special cradles or carriages designed for

chlorine equipment are used for lifting cylinders;

b. Proper storage of containers;

c. Tag empty containers, and store separate from full cylinders;

d. Use cylinders in order that they are received;

e. Use ONLY approved tools;

f. Cylinder emergency repair kits should be readily available;

2. Emergency Procedures and Emergency Equipment.

a. Written procedures in event of catastrophic leak or container rupture.

b. Self-contained pressure helmets; with own compressed air supply and full-face piece;

located at readily accessible points, away from area(s) likely to be contaminated with

chlorine gas.

c. Spare cylinders on site for use during prolonged emergencies.

d. Inspect helmets, emergency kits, and breathing air supply tanks routinely.

e. Formal training with drills for potential users of helmets and emergency equipment.

3. Leak Detection

a. A strong solution of aqueous ammonia is available for use in locating source of leaks

b. Repairs of chlorine leaks are to be done by at least two people. Protecting gear should

be used, and if below grade, safety harnesses and ropes are worn and emergency

rescue operators are present.

c. Piping and valves in chlorine rooms should be color coded and labeled for rapid

identification.

d. Properly train repair people.

WARWS can help: We are ready to help you complete your O&M Manual, please call or office or contact your Water Circuit Rider for assistance.

This format / template is the property of WARWS, has been produced as membership benefit to assist Members at NO CHARGE, and shall not be repackaged for resale to another entity or person. WARWS  reserves the right, at it’s sole discretion, to limit or deny access to those who might use this work product for profit or otherwise misuse or abuse this FREE member benefit. This template is intended for use by small water systems and may be modified to fit the specific needs of each system.